Test System No.3

A 13-Bus Balanced Industrial Distribution System

This test case consists of 13 buses and is representative of a medium-sized industrial plant.  The system is extracted from a common system that is being used in many of the calculations and examples in the IEEE Color Book series.  The plant is fed from a utility supply at 115 kV and the local plant distribution system operates at 13.8 kV.  The system is shown in Figure 3.1 and described by the data in Tables 3.1-4.  Due to the balanced nature of this example, only positive sequence data is provided.  Capacitance of the short overhead line and all cables are neglected.

Figure 3.1.  Test System 3 - A balanced industrial system.

Table 3.1. Per-Unit Line and Cable Impedance Data

(base values: 13.8 kV, 10,000 kVA)

| From | To | R | X |
| --- | --- | --- | --- |
| 100: UTIL-69 | 01:69-1 | 0.00139 | 0.00296 |
| 03:MILL-1 | 50:GEN-1 | 0.00122 | 0.00243 |
| 03:MILL-1 | 05:FDR F | 0.00075 | 0.00063 |
| 03:MILL-1 | 26:FDR G | 0.00157 | 0.00131 |
| 03:MILL-1 | 06:FDR H | 0.00109 | 0.00091 |

Table 3.2. Transformer Data

| From | To | Voltage | Tap | kVA | %R | %X |
| --- | --- | --- | --- | --- | --- | --- |
| 01:69-1 | 03:MILL-1 | 69:13.8 | 69 | 15000 | 0.4698 | 7.9862 |
| 50:GEN1 | 51:AUX | 13.8:0.48 | 13.45 | 1500 | 0.9593 | 5.6694 |
| 05:FDR F | 49:RECT | 13.8:0.48 | 13.45 | 1250 | 0.7398 | 4.4388 |
| 05:FDR F | 39:T3 SEC | 13.8:4.16 | 13.11 | 1725 | 0.7442 | 5.9537 |
| 26:FDR G | 29:T11 SEC | 13.8:0.48 | 13.45 | 1500 | 0.8743 | 5.6831 |
| 06:FDR H | 11:T4 SEC | 13.8:0.48 | 13.8 | 1500 | 0.8363 | 5.4360 |
| 06:FDR H | 19:T7 SEC | 13.8:2.4 | 13.11 | 3750 | 0.4568 | 5.4810 |

Table 3.3. Generation, Load, and Bus Voltage Data

(from power flow study results)

| Bus | Vmag (p.u.) |  (deg) | Pgen kW | Qgen kvar | Pload kW | Qload kvar |
| --- | --- | --- | --- | --- | --- | --- |
| 100:UTIL-69 | 1.000 | 0.00 | 7450 | 540 | - | - |
| 01:69-1 | 0.999 | -0.13 | - | - | - | - |
| 03:MILL-1 | 0.994 | -2.40 | - | - | 2240 | 2000 |
| 50:GEN1 | 0.995 | -2.39 | 2000 | 1910 | - | - |
| 51:Aux | 0.995 | -3.53 | - | - | 600 | 530 |
| 05:FDR F | 0.994 | -2.40 | - | - | - | - |
| 49:RECT | 0.980 | -4.72 | - | - | 1150 | 290 |
| 39:T3 SEC | 0.996 | -4.85 |  |  | 1310 | 1130 |
| 26:FDR G | 0.994 | -2.40 | - | - | - | - |
| 06:FDR H | 0.994 | -2.40 | - | - | - | - |
| 11:T4 SEC | 0.979 | -3.08 | - | - | 370 | 330 |
| 19: T7 SEC | 1.001 | -4.69 | - | - | 2800 | 2500 |
| 29:T11 SEC | 0.981 | -4.16 | - | - | 810 | 800 |

Table 3.4. Harmonic Source Data

| Harmonic # | Percent | Relative Angle |
| --- | --- | --- |
| 1 | 100.00 | 0.00 |
| 5 | 18.24 | -55.68 |
| 7 | 11.90 | -84.11 |
| 11 | 5.73 | -143.56 |
| 13 | 4.01 | -175.58 |
| 17 | 1.93 | 111.39 |
| 19 | 1.39 | 68.30 |
| 23 | 0.94 | -24.61 |
| 25 | 0.86 | -67.64 |
| 29 | 0.71 | -145.46 |
| 31 | 0.62 | 176.83 |
| 35 | 0.44 | 97.40 |
| 37 | 0.38 | 54.36 |

Additional data used to conduct a harmonic analysis of the example industrial system include the following:

- System equivalent impedance.  For this study, the system impedance was determined from the fault MVA and X/R ratio at the utility connection point.  These values are 1000 MVA and 22.2, respectively.  Driving point impedance at the connection point was not available, but should be used whenever possible.

- The local (in-plant) generator was represented as a simple Thevenin equivalent.  The internal voltage, determined from the converged power flow solution, is 13.98/-1.52° kV.  The equivalent impedance is the sub-transient impedance which is 0.0366+j1.3651.

- The plant power factor correction capacitors are rated at 6000 kvar.  As is typically done, leakage and series resistance of the bank are neglected in this study.

- The displacement power factor for the drive load is 0.97 lagging.  This high power factor is typical of drives operated at or near full load.

Specific issues related to modeling for harmonic analysis must also be considered if the results presented here are to be obtained using different analysis programs.  Modeling considerations applicable to this example include:

- All loads are modeled as series RL circuits.  This approach is taken instead of parallel RL modeling to more accurately represent the limited harmonic damping offered by typical induction motors without resorting to extremely detailed motor models.

- Frequency dependence of model resistance is neglected.  This is done mainly because of the significant discrepancies that exist among various programs available.  In addition, neglecting frequency effects on resistance leads to over conservative results (which are often preferred).

- Transformer magnetizing branch effects are neglected.  In addition, increasing winding losses as a function of frequency are also neglected.  As discussed in 2 previously, this is done to avoid problems when comparing the results presented here with those obtained using other analysis programs.

The results of a harmonic analysis of the system of Figure 3.1 are given in Table 3.5.  Fundamental, fifth, and seventh voltage harmonic amplitudes and THDV are given for each of the system buses. These results, along with those obtained from a fundamental frequency power flow (shown in Table 3.3), give an accurate description of the voltage profiles in the plant.

Table 3.5 Plant Voltage Harmonic Summary

| Bus | V1 (VLN) | V5 (VLN) | V7 (VLN) |  | THDV (%) |
| --- | --- | --- | --- | --- | --- |
| 100:UTIL-69 | 39645.70 | 40.37 | 104.23 | 0.28 |  |
| 01:69-1 | 39538.00 | 52.36 | 135.14 | 0.37 |  |
| 03:MILL-1 | 7712.77 | 53.51 | 138.13 | 1.93 |  |
| 50:GEN1 | 7726.55 | 51.72 | 133.51 | 1.87 |  |
| 51:Aux | 262.74 | 1.72 | 4.40 | 1.81 |  |
| 05:FDR F | 7709.24 | 54.07 | 138.35 | 1.94 |  |
| 49:RECT | 269.89 | 12.79 | 12.83 | 8.02 |  |
| 39:T3 SEC | 2240.05 | 14.83 | 37.21 | 1.80 |  |
| 26:FDR G | 7709.07 | 53.48 | 138.04 | 1.93 |  |
| 06:FDR H | 7703.35 | 53.43 | 137.91 | 1.93 |  |
| 11:T4 SEC | 260.40 | 1.78 | 4.59 | 1.90 |  |
| 19: T7 SEC | 1302.74 | 8.58 | 21.78 | 1.81 |  |
| 29:T11 SEC | 256.29 | 1.71 | 4.36 | 1.84 |  |