4th Harmonic Test System: Unbalanced Commercial System

please send your questions and comments to

Wilsun Xu (wxu@ee.ualberta.ca)

Equivalent 480V Supply System:

Three-phase fault level:	5000kVA	R/X=0.3

Single-phase fault level:	1000kVA	R/X=0.5

Transformer (480/120): 	100kVA,	5%,	Delta/Yg

Three single-phase concentric cables:

phase cable:	0.0004+j0.0005 ohm/meter

neutral cable:	0.0025+j0.0040 ohm/meter

length:		20 meters

Motor and equivalent linear load:

Motor cable:	Zs=0.00644+j0.0036 ohm,;	Zm=0.00230+j0.001ohm;

Motor load:	Zs=j2.88 ohm,;		Zm=j0.72ohm; 		5000+j1500 VA;

Linear load:	Sa= 3000+j0 VA;		Sb=2000+j0 VA;		Sc = 3500+j0 VA;

Office equipment

Phase A:	Sload1=10,000+j500 VA; 	Sload2=5,000+j1500 VA; 	cable length = 50m

Phase B:	Sload1=  9,000+j400 VA; 	Sload2=4,000+j1000 VA;	cable length = 30m

Phase C:	Sload1=  5,000+j400 VA; 	Sload2=7,000+j2000 VA;	cable length = 60m

Phase cable:	0.0004+j0.0005 ohm/meter

Neutral cable:	0.0016+j0.0010 ohm/meter

Harmonic spectra of office equipment

|  | Load 1 |  | Load 2 |  |
| --- | --- | --- | --- | --- |
| H | Mag | Angle | Mag | Angle |
| 1 | 1 | -37 | 1 | -37 |
| 3 | 0.657 | -97 | 0.199 | -63 |
| 5 | 0.377 | -166 | 0.074 | 137 |
| 7 | 0.127 | 113 | 0.032 | 30 |
| 9 | 0.044 | -46 | 0.024 | -108 |
| 11 | 0.053 | -158 | 0.018 | 168 |
| 13 | 0.025 | 92 | 0.008 | 68 |
| 15 | 0.019 | -51 | 0.004 | -48 |
| 17 | 0.018 | -151 | 0.001 | -125 |
| 19 | 0.011 | 84 | 0.002 | -66 |

Zero sequence filter

The filter is modeled as 6 coupled windings, R=0 is assumed for all windings. The following table lists the coupled X values of the windings in ohms. The windings can be connected to form a Yg/D filter or a Zigzag filter.

|  | W1 | W2 | W3 | W4 | W5 | W6 |
| --- | --- | --- | --- | --- | --- | --- |
| W1 | 1.0061 |  |  |  |  |  |
| W2 | -0.4411 | 1.0061 |  |  |  |  |
| W3 | -0.4411 | -0.4411 | 1.0061 |  |  |  |
| W4 | 0.9984 | -0.4416 | -0.4416 | 1.0061 |  |  |
| W5 | -0.4416 | 0.9984 | -0.4416 | -0.4411 | 1.0061 |  |
| W6 | -0.4416 | -0.4416 | 0.9984 | -0.4411 | -0.4411 | 1.0061 |

Sample Results:

Figure 9.9 shows the waveforms of the neutral voltage at the receptacle panel. The waveform obtained without harmonic trapper is also displayed in the figure for comparison purposes. It can be seen from the figure that the neutral voltage can be quite high (about 20V RMS) if no mitigation measures are taken. The harmonic trappers can reduce the voltage to as little as 3V RMS. The neutral voltage is dominated by the 3rd harmonic component. The results also shown that -Y and zigzag configurations have almost the same effect in terms of reducing the neutral voltage (the waveforms are indistinguishable in Figure 9.9).

Figure 9.9.  Neutral voltage at the receptacle panel

Table 9.2.  Harmonic trapper winding currents

and conductor neutral currents (A)

|  |  | W-1 | W-2 | W-3 | W-4 | W-5 | W-6 |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | I1 | 80.5 | 93.0 | 75.8 | 9.8 | 9.8 | 9.8 |
| Y-D | Ih-rms | 53.8 | 53.8 | 53.6 | 50.0 | 50.0 | 50.0 |
|  | Irms | 96.9 | 107.4 | 92.8 | 50.9 | 50.9 | 50.9 |
|  | I1 | 26.8 | 37.9 | 21.6 | 37.9 | 21.6 | 26.7 |
| Zigzag | Ih-rms | 53.6 | 53.6 | 53.6 | 53.6 | 53.6 | 53.6 |
|  | Irms | 59.9 | 65.6 | 57.8 | 65.6 | 57.8 | 59.9 |
|  |  | No harmonic source |  |  |  | 38.2 |  |
| Neutral |  | With h-source but no trapper |  |  |  | 187.0 |  |
| current |  | with Y- trapper |  |  |  | 22.8 |  |
| (RMS) |  | with Zigzag trapper |  |  |  | 23.5 |  |

Table 9.2 lists the loading conditions, in the form of winding currents,  associated with both configurations. It can be seen from the table that the zigzag configuration results in smaller RMS winding currents. The Y- configuration is therefore less desirable in terms of losses and device overheating. The neutral conductor currents in RMS values were also calculated for various configurations and are shown in the same table. The entry of “No harmonic source” is the current obtained with the assumption that loads do not contain harmonic sources. The results suggest that the increase of neutral current is mainly due to the harmonic currents from the loads. Due to space limitations, other important issues such as transformer de-rating and harmonic injections into the supply system are not discussed. They can be easily investigated using the same system model and analysis tool.